| Project Name | Click or tap here to enter text. |  |  | ICRA Number |  | Click or tap here to enter text. |
| --- | --- | --- | --- | --- | --- | --- |
| Description | Click or tap here to enter text. |  |  |  |  |  |
| Project Location | Click or tap here to enter text. |  | Project Start Date |  | Click or tap to enter a date. |  |
| Estimated Duration |  | Click or tap here to enter text. | Expiration Date |  | Click or tap to enter a date. |  |
| Facility Project Manager |  | Click or tap here to enter text. | Phone |  | Click or tap here to enter text. |  |
| Supervisor |  | Click or tap here to enter text. | Phone |  | Click or tap here to enter text. |  |
| Contractor / Vendor |  | Click or tap here to enter text. | Phone |  | Click or tap here to enter text. |  |

| - Construction Activity – Explain Reasoning for Assessment / Choice |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | ☐ | Type A | ☐ | Type B | ☐ | Type C | ☐ | Type D |
| Click or tap here to enter text. |  |  |  |  |  |  |  |  |

| - Patient Risk – Describe Key Patient Risks |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | ☐ | Low | ☐ | Medium | ☐ | High | ☐ | Highest |
| Click or tap here to enter text. |  |  |  |  |  |  |  |  |

| - Class of Precautions |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Type A |  | Type B |  | Type C |  | Type D |
| Low | ☐ | I | ☐ | II | ☐ | II | ☐ | III |
| Medium | ☐ | I | ☐ | II | ☐ | III | ☐ | IV |
| High | ☐ | I | ☐ | III | ☐ | IV | ☐ | V |
| Highest | ☐ | III | ☐ | IV | ☐ | V | ☐ | V |

| - Surrounding Areas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Below |  |  | Above |  | Lateral |  | Behind |  | In Front |  |
| Unit |  |  |  | Click or tap here to enter text. |  |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  |
| Risk Group |  |  |  | Click or tap here to enter text. |  |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  |
| Contact |  |  |  | Click or tap here to enter text. |  |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  |
| Phone |  |  |  | Click or tap here to enter text. |  |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  | Click or tap here to enter text. |  |
| Controls |  |  |  | ☐ |  | Noise | ☐ | Noise | ☐ | Noise | ☐ | Noise | ☐ | Noise |
|  |  |  |  | ☐ |  | Vibration | ☐ | Vibration | ☐ | Vibration | ☐ | Vibration | ☐ | Vibration |
|  |  |  |  | ☐ |  | Dust | ☐ | Dust | ☐ | Dust | ☐ | Dust | ☐ | Dust |
|  |  |  |  | ☐ |  | Ventilation | ☐ | Ventilation | ☐ | Ventilation | ☐ | Ventilation | ☐ | Ventilation |
|  |  |  |  | ☐ |  | Pressurization | ☐ | Pressurization | ☐ | Pressurization | ☐ | Pressurization | ☐ | Pressurization |
| Systems Impacted |  |  |  | ☐ |  | Data | ☐ | Data | ☐ | Data | ☐ | Data | ☐ | Data |
|  |  |  |  | ☐ |  | Mechanical | ☐ | Mechanical | ☐ | Mechanical | ☐ | Mechanical | ☐ | Mechanical |
|  |  |  |  | ☐ |  | Med Gas | ☐ | Med Gas | ☐ | Med Gas | ☐ | Med Gas | ☐ | Med Gas |
|  |  |  |  | ☐ |  | Hot/Cold H20 | ☐ | Hot/Cold H20 | ☐ | Hot/Cold H20 | ☐ | Hot/Cold H20 | ☐ | Hot/Cold H20 |
|  |  |  |  | ☐ |  | Other | ☐ | Other | ☐ | Other | ☐ | Other | ☐ | Other |
| Were there discoveries in surrounding areas that would serve as cause to increase the class of precautions and necessitate additional controls? If so, please summarize |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ☐ | Yes | ☐ | No |  | Click or tap here to enter text. |  |  |  |  |  |  |  |  |  |

| - Approval |  |  |  |
| --- | --- | --- | --- |
| Additional Requirement(s): | Click or tap here to enter text. |  |  |
| Permit Requested by | Click or tap here to enter text. | Date | Click or tap to enter a date. |
| Permit Authorized By | Click or tap here to enter text. | Date | Click or tap to enter a date. |

| CLASS | ✓ | CLASS MITIGATION OPTIONS Select measures required for this project based on the class of precautions, work activity, surrounding risk, and site-specific conditions. Not every listed measure will apply to every project. |
| --- | --- | --- |
| I | ☐ | This class of precautions is used for noninvasive work only. |
|  | ☐ | Perform noninvasive work, without blocking or interrupting patient care, outside directly occupied patient areas. |
|  | ☐ | Perform work using methods that do not generate dust |
|  | ☐ | Replace ceiling tile immediately. |
|  | ☐ | No HVAC adjustments required. |
| II | ☐ | This Class of Precautions must never be used for construction or renovation activities. |
|  | ☐ | Perform only limited dust work and/or activities designed for basic facilities and engineering work per facility procedures. |
| III | ☐ | Install active systems (e.g., negative air machines) to prevent dust from entering occupied areas |
|  | ☐ | Use dust-control methods such as HEPA vacuuming, plastic containment, or closing the room door. |
|  | ☐ | Water mist work surfaces to control dust while cutting. |
|  | ☐ | Remove or isolate return air diffusers to prevent dust from entering the HVAC system. |
|  | ☐ | Remove or isolate supply air diffusers to prevent positive pressurization of the work area. |
|  | ☐ | Seal all doors and openings as needed with tape that will not leave residue. |
|  | ☐ | If the work area is contained, maintain neutral-to-negative pressure. |
|  | ☐ | Contain all trash and debris inside the construction zone. |
|  | ☐ | Transport debris in nonporous, smooth, cleanable containers with hard lids. |
|  | ☐ | Damp-wipe all containers to ensure they are free of visible dust and debris before removing them from the work area. |
|  | ☐ | Install adhesive dust-control mats at the entrance to the contained work area. |
|  | ☐ | Change adhesive dust-control mats routinely and when visibly soiled. |
|  | ☐ | Damp mop or HEPA vacuum surrounding areas when the work area is not fully contained. |
| IV | ☐ | Apply applicable Class III debris-control and housekeeping measures. |
|  | ☐ | Consider particulate monitoring to ensure contaminants do not enter occupied areas. |
|  | ☐ | Use solid barriers, meeting NFPA 241/fire safety codes, that extend to the ceiling or, if ceiling tile is removed, to the deck above. |
|  | ☐ | Ensure plastic or hard barriers are tightly secured to the ceiling and floor. |
|  | ☐ | If using plastic barriers, apply tape that will not leave a residue to seal gaps between barriers, ceiling, or floor. |
|  | ☐ | Close all gaps in the barrier (walls, floor, ceiling) using approved firestop materials. |
|  | ☐ | For small work areas, use an approved containment unit with HEPA-filtered exhaust when appropriate. |
|  | ☐ | Remove or isolate return air diffusers to prevent dust from entering the HVAC system. |
|  | ☐ | Remove or isolate supply air diffusers to prevent positive pressurization of the work area. |
|  | ☐ | Negative airflow pattern must be maintained from the entry point to the anteroom and into the construction area. |
|  | ☐ | Maintain negative pressurization of the entire workspace by use of HEPA exhaust air systems directed outdoors. |
|  | ☐ | Outdoor exhaust discharged ≥25 feet from entrances, air intakes, and windows does not require HEPA filtration. |
|  | ☐ | If exhaust is directed indoors, use HEPA filtration with ≥99.97% efficiency without altering adjacent airflow/pressure. |
|  | ☐ | Exhaust into shared or recirculating HVAC systems, or other shared exhaust systems (e.g., bathroom exhaust) is not acceptable. |
|  | ☐ | Use a device outside containment to continuously monitor negative pressure; use a visual indicator when available. |
|  | ☐ | Do not track dust or debris outside containment; HEPA vacuum clothing or use cover suits as needed. |
|  | ☐ | Workers must wear shoe covers prior to entry into the work area. |
|  | ☐ | Shoe covers must be changed when damaged and prior to exiting the anteroom to the occupied space. |
| V | ☐ | Apply all applicable Class IV controls, plus the measures below. |
|  | ☐ | Construct an anteroom adjacent to the work area for personnel, equipment staging, and cart cleaning. |
|  | ☐ | Seal all containment and anteroom penetrations, including floors and ceilings, with approved materials; use UL-rated firestop when applicable. |
|  | ☐ | Personnel are required to wear disposable coveralls during Class V work; coveralls must be removed before exiting the anteroom. |
|  | ☐ | Prior to the start of work, HEPA filtration must be verified by particulate measurement at no less than 99.97% efficiency and must not alter or change airflow/pressure relationships in other areas. |

Environmental conditions that could affect human health, such as sewage, mold, asbestos, gray water and black water will require Class of Precautions IV for LOW and MEDIUM Risk Groups and Class of Precautions V for HIGH and HIGHEST Risk Groups.

*Type C [Medium Risk groups] and Type D [Low Risk Groups] work areas [Class III precautions] that cannot be sealed and completely isolated from occupied patient care spaces should be elevated to include negative air exhaust requirements as listed in Class IV Precautions.

Table 6 - Minimum Required Infection Control Precautions | Upon Completion of Work Activity

|  | Class of Precautions | Mitigation Activities |
| --- | --- | --- |
| ☐ | Classes I, II and III | Cleaning: - Clean work areas, including all environmental surfaces, high horizontal surfaces, and flooring materials at the end of each workday and upon project completion. - Check all supply and return air registers for dust accumulation on upper surfaces as well as air diffuser surfaces. HVAC Systems: - Remove isolation of the HVAC system in areas where work is being performed. - Verify that HVAC systems are clean and operational. - Verify the HVAC systems meet original airflow and air exchange design specifications. |
| ☐ | Classes III, IV and V | Class III (Type C Activities only), IV, and V precautions require inspection and documentation for downgraded ICRA precautions. Construction areas must be inspected by an infection preventionist or designee and engineering representative for discontinuation or downgrading of ICRA precautions. Work Area Cleaning: - Clean work areas, including all environmental surfaces, high horizontal surfaces and flooring materials at the end of each workday and upon project completion. - Check all supply and return air registers for dust accumulation on upper surfaces as well as air diffuser surfaces. Removal of Critical Barriers: - Critical barriers must remain in place during all work involving drywall removal, creation of dust and activities beyond simple touch-up work. The barrier may NOT be removed until a work area cleaning has been performed. - All (plastic or hard) barrier removal activities must be completed in a manner that prevents dust release. Use the following precautions when removing hard barriers: - Carefully remove screws and painter tape. - If dust will be generated during screw removal, use hand-held HEPA vacuum. - Drywall cutting is prohibited during removal process. - Clean all stud tracks with HEPA vacuum before removing outer hard barrier. - Use a plastic barrier to enclose area if dust could be generated. Negative Air Requirements: - Negative air must effectively remove contaminants from the work area. - Negative air devices must remain operational at all times and in place for a period after completion of dust-creating activities to remove contaminants from the work area and before removal of critical barriers. HVAC systems: - Upon removal of critical barriers, remove isolation of HVAC system in areas where work is being performed. - Verify that HVAC systems are clean and operational. - Verify the HVAC systems meet original airflow and air exchange design specifications. |

Appendix A: Construction & Renovation Type

| TYPE A | Inspection and noninvasive activities Includes, but is not limited to: Removal of ceiling tile for visual inspection-limited to 1 tile per 50 square feet with limited exposure time. Limited building system maintenance (e.g., pneumatic tube station, HVAC system, fire suppression system, electrical and carpentry work to include painting without sanding) that does not create dust or debris. Limited clean plumbing activity. |
| --- | --- |
| TYPE B | Small-scale, short duration activities that create minimal dust and debris Includes, but is not limited to: • Work conducted above the ceiling (e.g., prolonged inspection or repair of firewalls and barriers, installation of conduit and/or cabling, and access to mechanical and/or electrical chase spaces). Fan shutdown/startup. Installation of electrical devices or new flooring that produces minimal dust and debris. The removal of drywall where minimal dust and debris is created. Controlled sanding activities (e.g., wet or dry sanding) that produce minimal dust and debris. |
| TYPE C | Large-scale, longer duration activities that create a moderate amount of dust and debris Includes, but is not limited to: • Removal of preexisting floor covering, walls, casework or other building components. New drywall placement. Renovation work in a single room. Non-existing cable pathway or invasive electrical work above ceilings. The removal of drywall where a moderate amount of dust and debris is created. Dry sanding where a moderate amount of dust and debris is created. Work creating significant vibration and/or noise. Any activity that cannot be completed in a single work shift. |
| TYPE D | Major demolition and construction projects Includes, but is not limited to: Removal or replacement of building system component(s). Removal/installation of drywall partitions. Invasive large-scale new building construction. Renovation work in two or more rooms. |

Appendix B: Patient Risk Group

| LOW Non-patient care areas | - Office areas - Public hallways/gathering areas not on clinical units - Breakrooms, bathrooms, locker rooms, mechanical rooms, and EVS closets not on clinical units |
| --- | --- |
| MEDIUM Patient care support areas | - Waiting areas - Materials Management - Sterile Processing Department – dirty side - Kitchen, cafeteria, gift shop, coffee shop, food kiosks - Biomedical Engineering |
| HIGH Patient care areas | - Emergency Department - Labor & Delivery - Newborn Nursery - All acute-care units - Patient rooms and patient-care areas - Employee Health - Laboratories - Medication rooms and clean utility rooms - Pharmacy — general/nonsterile work areas - Diagnostic imaging areas (e.g., Cardiology/Echocardiology, MRI, Nuclear Medicine, and Radiology) - Physical Therapy - Respiratory Therapy |
| HIGHEST Procedural, invasive, sterile support and highly compromised patient care | - Intensive Care Units (e.g., ICU, CCU, NICU, PICU) - Oncology and transplant units - Operating rooms and restricted areas - Procedural suites (e.g., Endoscopy, Cardiac Cath Lab) - PACU - Invasive imaging - Pharmacy — sterile compounding - Sterile Processing Department — clean side - Transfusion Services - Dedicated isolation wards/units - Airborne Infection Isolation Rooms (AIIRs)/negative-pressure rooms, as designated by facility risk assessment - Other areas caring for highly immunocompromised patients |

Appendix C: Surrounding Area Mitigation Strategies

| Noise & Vibration Mitigation Strategies |  |
| --- | --- |
| ☐ | Use diamond drills instead of powder-actuated fasteners |
| ☐ | Schedule noise-making periods with adjacent spaces |
| ☐ | Use beam clamps instead of powder-actuated fasteners |
| ☐ | Prefab where possible |
| ☐ | Use tin snips to cut metal studs instead of using a chop saw |
| ☐ | Install metal decking with vent tabs, then use cellular floor deck hangers |
| ☐ | Consider compression style fittings instead of soldering, brazing, or welding |
| ☐ | Wet core drill instead of dry core or percussion |
| ☐ | Instead of jackhammering concrete, use wet diamond saws |
| ☐ | Use HEPA vacuums instead of standard wet/dry vacuums |
| ☐ | Use mechanical joining system sprinkler fittings instead of threaded |
| ☐ | Where fumes are tolerated, use chemical adhesive remover (flooring glue) instead of mechanical |
| ☐ | To remove flooring, consider abrasive blasting instead of using a floor scraper |
| ☐ | Use electric shears instead of a reciprocating saw for ductwork cutting |
| ☐ | Install exterior man/material lifts |
| Ventilation & Pressurization Mitigation Strategies |  |
| ☐ | HEPA-filter exhaust to exterior |
| ☐ | Install temporary ductwork |
| ☐ | Utilize temporary HVAC equipment |
| ☐ | Temporarily vacate the affected area |
| ☐ | Install temporary partitions |
| ☐ | Use carbon filtration to filter odors |
| Impact to Other Systems Mitigation Strategies |  |
| ☐ | Schedule outages |
| ☐ | Provide temporary systems |
| ☐ | Back-feed electricity or medical gases |

References:

- https://www.ashe.org/system/files/media/file/2022/08/ICRA%202.0%20Tool%20%2B%20Permit.pdf

- https://www.hfmmagazine.com/articles/4623-conducting-infection-control-risk-assessments-the-right-way

- https://vertexeng.com/insights/best-practices-discussing-icra-2-0-in-healthcare/

- https://www.ashe.org/icra2

- https://www.ashe.org/education/icra-elearning